## UASB
GUIDANCE METHODOLOGY
1 a) DESIGN PHASE - TECHNICAL DATA
HYDRO 1 Facility n° | TECHNOLOGIES INVOLVED |  |  | Legend
1) | Upflow Anaerobic Sludge Blanket |  |  |  | Design Data which should be provided by the site manager
2) | Constructed Wetland |  |  |  | Assumed Data for Design
3) | Membrane/Sand Filtration + UV Disinfection
4) | Composting system
Design Data UASB
Parameters | Units | Typical | Used for HYDRO 1 in Greek Case Study | Insert Data according to Replication Site Case Study | Notes
Influent Wastewater Charateristics:
Population equivalent to be served | PE |  | 500
Flowrate | m3/d | - | 100
COD concentration | mg/l | 500 | 578
BOD5 concentration | mg/l | 300 | 331
TSS concentration | mg/l | 320 | 272
Organic Load | kg COD/d | - | 57.8
pH | - | - | 7.3
Conductivity | μS/cm | - | 1164
TKN | mg/l | 40 | 42
Ammonia Concentration | mg/l | 25 | 32
Temperature | °C | - | 23
Operative Parameters:
HRTdesign | h | 5 ÷ 10 | 10 |  | Set as hypothesis
Volume tot | m3 | - | 41.6667
n° of operative lines | n° | - | 2
Volume of each line | m3 | - | 20.8333
OLR | kg COD/m3 d | 0.8-2 | 1.3872
HRToperative | h | - | 10
Vup | m/h | 0.5 - 1.5 | 0.6
Area (each reactor sectional area) | m2 | - | 3.4722
Diameter | m | - | 2.1026
Each Reactor height | m | - | 6
Liquid upflow velocity at the bottom of the GLS separator (VUP,GLS) | m/h | < 4 | 1 |  | Set as hypothesis
Sliq (each reactor Liquid Area) | m2 | - | 2.0833
Sliq (each reactor separation Area) | m2 | - | 1.3889
dsep (each reactor separation diameter) | m |  | 1.3298
Stoichiometrically methane production | m3CH4/kgCODRemoved | 0.35 | 0.35
COD removal | % | 70 - 80 | 70
COD removed | kgCOD/d | - | 40.46
Daily methane production | m3CH4/d | - | 14.161
Methane percentage in the Biogas | %CH4/biogas | 60 | 60
Daily Biogas production | m3biogas/d | - | 23.6017
Stoichiometrically Sludge production | kg sludge/kg CODRemoved | 0.06 - 0.07 | 0.062
Sludge production | kg sludge/d | - | 2.5085
TS% of sludge | mgTSS/l | - | 20000 |  | Set as hypothesis
Q excess sludge | m3/d | - | 0.12543
UASB Balance
Qout | m3/d | - | 99.8746
CODin | kgCODin/d | - | 57.8
CODout | kgCODout/d | - | 17.34
| mg/l | - | 173.6178
TSS in | kgTSS/d | - | 27.2
TSS removal | % | 60 - 70 | 67
TSS removed | kdTSS/d | - | 18.224
TSSout | kgTSSout/d | - | 8.976
| mg/l | - | 89.8727
Energy Conversion factor | kJ/kWh | 3599.9712 | 3599.9712 |  | Set as default data
Energy content of methane at standard conditions | kJ/m3CH4 | 35846 | 35846 |  | Set as default data
Energy production | kW/m3 |  | 1.4101
| kW/d |  | 141.0054
MASS AND ENERGY BALANCE |  |  |  |  | *Waste indicates any generic residual/or untreated flow which could be derived by the process
| INPUTs |  | OUTPUTs |  | If any, please indicate the type and the amount
Wastewater to be treated [m3/d] = |  |  | UASB supernatant [m3/d] =
Excess Sludge [m3/d] =
Maximum Energy Needed [kWh/d] = |  |  | Energy Produced [kW/d] = |  | if any
Waste* [.../d] =
Technical minimum requirement to Technology replicability:
FOOTPRINT
Paramenter to analyse | Unit | Specification | TOTAL | Notes
Equipment area requirement | m2 | UASB reactor
Tanks
Area required for piping
Heating/Cooling systems - Electric resistance
Gasometer
|  | Combined Heat and Power system (CHP) |  | For Biogas convertion into electricity and thermal energy
PLC
….......
Total area requirement | m2 | Considering all of the equipments (tanks. pumps. piping. etc...) | 0
Specific area equirement | m2/(m3treated/d) | m2 per m3/day of wastewater treated | 0.4445 | From Greek Case Study
INPUTS (Requirements)
Paramenter to analyse | Unit | Specification | TOTAL | Notes
Influent Flowrate | m3/d | Municipal Wastewater
Maximum Energy Consumption | kWh/d | Energy for: | kW absorbed | h/d | kWh/d | kW*h/d
|  | pumps |  |  | 0
|  | For Heating/Cooling systems - Electric resistance |  |  | 0
|  | CHP |  |  | 0
|  | Mixing systems |  |  | 0
…....................
|  | TOTAL requirements |  |  | 0
Specific Energy consumption | kWh/m3 treated | Specific kWh consumed/day per m3/day of wastewater treated | - | - | 1.9584 |  | From Greek Case Study
Reagents Consumption | l/d | Considering reagents both for operation and maintenance (cleaning)
COSTS (CAPEX)
Paramenter to analyse | Unit | Specification | TOTAL | Notes
Cost of units | € | Tanks | 0
| € | UASB Reactor | 0
| € | Pumps | 0
| € | Gasometer | 0
| € | Heating/cooling system - Electric resistance | 0
| € | CHP | 0
| € | Piping, cables, valves | 0
| € | Sensors, PLC | 0
Construction/Installation of units | € | Preparation of site | 0
| € | Installation | 0
Total CAPEX | € |  | 0
TOTAL CAPEX | €/PE |  | 543 | From Greek Case Study
COSTS (OPEX)
Paramenter to analyse | Unit | Specification | Amount used | Unit Value | Total Cost | Notes
Reagents | €/y | Considering reagents both for operation and maintenance (cleaning) |  |  |  | l/y*€/l
Energy costs | €/y | Considering cost of electricity [average between day and night, during week and week-end] | 0 | 0.17 | 0 | kWh/y * €/kWh(=0,17 average in Europe for non-household elecrticity)
Human Requirement | €/y | Considering personnel both for operation and maintenance |  |  | 0 | Hour of work required/y * €/h
Maintenance | €/y | Considering substitution of pieces etc… |  |  | 0 | Quantity of unit to change/y * €/unit
TOTAL ANNUAL OPEX | €/y |  | - | - | 0
TOTAL ANNUAL OPEX | €/y/PE |  |  |  | 79 |  | From Greek Case Study
OUTPUTS EXPECTED
Paramenter to analyse | Unit | Specification | TOTAL | Notes
Effluent Flowrate from UASB | m3/d | Biogas
| kWhth/d | Thermal Energy
| kWhel/d | Electricity
| m3/d | Nutrient rich effluent
| m3/d | Excess sludge
kgSS/d
SYSTEM

## CW
GUIDANCE METHODOLOGY
1 a) DESIGN PHASE - TECHNICAL DATA
HYDRO 1 Facility n° | TECHNOLOGIES INVOLVED |  |  | Legend
1) | Upflow Anaerobic Sludge Blanket |  |  |  | Design Data which should be provided by the site manager
2) | Biogas Upgrading System |  |  |  | Assumed Data for Design phase
3) | Constructed Wetland
4) | Membrane/Sand Filtration + UV Disinfection
5) | Composting system
Design Data CONSTRUCTED WETLAND
Parameters | Units | Typical | Used for HYDRO 1 in Greek Case Study | Insert Data according to Replication Site Case Study | Notes
Population equivalent to be served | PE |  | 500
Influent Wastewater Charateristics:
Flowrate | m3/d | - | 99.8746
COD concentration | mg/l | - | 173
BOD5 concentration | mg/l | - | 99.4
COD/BOD5 | - | - | 1.7404
TSS concentration | mg/l | - | 90
TSS loading rate | kg TSS/d | - | 8.9887
Organic Load in | kg BOD5/d | - | 9.9275
pH | - | - | 7.3
Conductivity | μS/cm | -
TKN concentration | mg/l | - | 42
TKN load in | kg/d | - | 4.1947
Ammonia Concentration | mg/l | - | 32
Temperature | °C | - | 23
Construction of CW System
Vertical Flow SAT
Bottom surface area | m2 |  | 250
Total Depth of filter media | m | 0,8 ÷ 1,5 | 1 |  | Set as Hypothesis
Free board | m |  | 0.3
Hydraulic retention time | d | > 0.7 days (considering pore volume of the media - common value equal to 0.35) | 0.7
5-10 mm round washed gravel | m | about 10 % of the filter media depth | 0.1
10-20 mm round washed gravel | m | about 10 % of the filter media depth | 0.1
30-50 mm round washed gravel | m | about 80 % of the filter media depth | 0.8
Total Depth | m |  | 1.3
Type of plants | - | To be chosen according to the climate | Phragmites australis
Bed slope | % | 0,1 ÷ 1 | 1
Vertical Flow UNSAT
Bottom surface area | m2 |  | 600
Total Depth of filter media | m | 0,8 ÷ 1,5 | 1 |  | Set as Hypothesis
Free board | m |  | 0.3
5-10 mm round washed gravel | m | about 20 % of the filter media depth | 0.2
0.4-5 mm sand | m | about 40 % of the filter media depth | 0.4
5-10 mm round washed gravel | m | about 20 % of the filter media depth | 0.2
20-40 mm round washed gravel | m | about 20 % of the filter media depth | 0.2
Total Depth | m |  | 1.3
Type of plants | - | To be chosen according to the climate | Phragmites australis
Bed slope | % | 0,1 ÷ 1 | 1
Lenght of VF sector | m |  | 18 |  | Dimensions given
Width of VF sector | m |  | 8.5
n° of sector | n° |  | 2
n° of bed per sector | n° |  | 2
Area of VF per sector | m2 |  | 306
Area of VF total (net) | m2 |  | 612
V pumping station | m3 |  | 3.5
Flush volume per sector | m3 |  | 3.1
n° of flush per day | n° |  | 9
Pump flow rate per sector | m3/h |  | 77
| l/s |  | 21.3889
Flush duration | min |  | 4.8
Flush time interval | h |  | 2.7
Operative Parameters VF UNSAT
TKN removal | % | 60 - 70 | 50 |  | Set as design value
TN removal | % |  | 5 |  | Set as design value
BOD5 removal | % |  | 90 |  | Set as design value
COD removal | % |  | 90 |  | Set as design value
TSS removal | % | See the loading graph on the right (verify the removal with the Ctss,in and TSS load,in) | 75 |  | Set as design value
Faecal and Total Coliforms removal | % | 98 - 99 |  |  | Set as design value
Viruses removal | % | 95 - 99 |  |  | Set as design value
Helminth Eggs | % | 93 - 99 |  |  | Set as design value
Hydraulic Loading Rate (batch) | m3/m2h |  | 0.25
| m3/m2d | from 0,04-0,05 without recircultation to 0,12 with recirculation | 0.12
Specific surface of total CW | m2/PE | To be checked function of organic loading rate limit Rule of thumb values: 3-5 m2/PE for passive systems, 1 m2/PE for intensified aerated systems | 1.7
Organic Loading Rate | gBOD5/m2d | To avoid clogging issues Passive wetland: if high touristic fluctuation < 20; if constant yearly flow rate < 10 Aerated wetland: <70 | 16.7
OTR | g O2/m2d | 23 - 64 | 32
TSS removal | % | See the loading graph on the right (verify the value with the value) | 75
HRT | h | from 3 to 6
Flushed volume on top VF surface | cm | from 2 to 4 | 2
Hydraulic Loading Rate | m3/m2/d | To avoid clogging issues Passive wetland: if high touristic fluctuation < 160; if constant yearly flow rate < 80 Aerated wetland: higher and driven by maximum organic loading rate | 0.16319
CW Performances | [5 empty] | Summer
Solids Loading Rate | gTSS/m2d | from 5 to 10 | 14.6874
Organic Loading Rate | gBOD5/m2d | To avoid clogging issues Passive wetland: if high touristic fluctuation < 20; if constant yearly flow rate < 10 Aerated wetland: <70 | 16.2215
BOD5 removed | kg/d |  | 8.9348
BOD5 out from CW | mg/l |  | 9.94
| kg/d |  | 0.99275
TKN removed | kg/d |  | 2.0974
TKN out from CW | mg/l |  | 21
| kg/d |  | 2.0974
Oxygen Demand | kgO2/d |  | 18.5827
TSS removed | kg/d |  | 6.7415
TSSout | kg/d |  | 2.2472
| mg/l |  | 22.5
MASS AND ENERGY BALANCE
| INPUTs |  | OUTPUTs |  |  | *Waste indicates any generic residual/or untreated flow which could be derived by the process
Wastewater to be treated [m3/d] = | 99.8746 |  | CW effluent [m3/d] = |  |  | If any, please indicate the type and the amount
Maximum Energy Needed [kWh/d] = | 0 |  | Energy Produced [kW/d] = | 0 | if any
Technical minimum requirement to Technology replicability:
FOOTPRINT
Paramenter to analyse | Unit | Specification | TOTAL | Notes
Equipment area requirement | m2 | VF SAT 1
VF UNSAT A, B
VF UNSAT C - D
area required for piping
PLC
Specific net CW area equirement | m2/(m3treated/d) | m2 per m3/day of wastewater treated | 8.4606 | From Greek Case Study
Total net CW area requirement | m2 | Effective area for treatment of wastewater by wetland beds | 845
Specific gross CW area coefficient | - | m2 gross CW area/m2 net CW area | 2.96 | From Greek Case Study
Total net CW area requirement | m2 | Considering all of the equipments (tanks, pumps, piping, etc...) | 2501.2
INPUTS (Requirements)
Paramenter to analyse | Unit | Specification | TOTAL | Notes
Influent Flowrate | m3/d | Municipal Wastewater |  | -
Maximum Energy Consumption | kWh/d | Energy for: | kW absorbed | h/d | kWh/d | Notes
|  | pumps |  |  | 0 | kW*h/d
|  | PLC, sensors |  |  | 0
|  | …............................. |  |  | 0
|  | TOTAL requirements |  |  | 0
Specific Energy consumption | kWh/m3 treated | Specific kWh consumed/day per m3/day of wastewater treated | - | - | 0.073532 | From Greek Case Study
Reagents Consumption | l/d | Considering reagents both for operation and maintenance (cleaning) | None
OUTPUTS EXPECTED
Paramenter to analyse | Unit | Specification | TOTAL | Notes
Evapotranspiration losses - VF SAT | m3/d | Summer value
Evapotranspiration losses - VF UNSAT | m3/d | Summer value
Effluent Flowrate from CW | m3/d | Effluent to be sent to UF + UV | 99.8746
Specific Evapotranspiration losses - VF SAT | m3/m2d | Summer value | 0
Specific Evapotranspiration losses - VF UNSAT | m3/m2d | Summer value | 0
Specific Evapotranspiration losses - VF SAT | m3/m2d | Summer value | 0.011 | From Greek Case Study
Specific Evapotranspiration losses - VF UNSAT | m3/m2d | Summer value | 0.005 | From Greek Case Study
COSTS (CAPEX)
Paramenter to analyse | Unit | Specification | TOTAL | Notes
Earthmoving | €/m3 | Parametric cost for: Excavate suitable material and place material in embankments
| m3 | Volume of excavate suitable material and place material in embankments |  | € = m2 * €/m2
| € | Cost of excavate suitable material and place material in embankments | 0
| €/m2 | Parametric cost for: Site clearance and top soil (max 20 cm) stripping
| m2 | Surface of site clearance and top soil (max 20 cm) stripping
| € | Cost of site clearance and top soil (max 20 cm) stripping | 0
| €/m3 | Parametric cost for: Compact embankment and trim to shape
| m3 | Volume of Compact embankment and trim to shape
| € | Cost for Compact embankment and trim to shape | 0
Filling material | €/m3 | Parametric cost for: Supply of washed gravel material (10 mm dia.), carbonate content < 20%, from approved quarry including transportation (Crushed or rounded)
| m3 | Volume of washed gravel material (10 mm dia.), carbonate content < 20%, from approved quarry including transportation (Crushed or rounded)
| € | Cost of washed gravel material (10 mm dia.), carbonate content < 20%, from approved quarry including transportation (Crushed or rounded) | 0
| €/m3 | Parametric cost for: Supply of washed river sand, D10 >0.3 mm D60 1-2 mm, carbonate content < 20%, from approved quarry including transportation
| m3 | Volume of washed river sand, D10 >0.3 mm D60 1-2 mm, carbonate content < 20%, from approved quarry including transportation
| € | Cost of river sand, D10 >0.3 mm D60 1-2 mm, carbonate content < 20%, from approved quarry including transportation | 0
Concrete works | €/m3 | Parametric cost for: preparation of lean concrete foundation reinforced by iron mesh
| m3 | Volume of lean concrete foundation reinforced by iron mesh
| € | Cost of lean concrete foundation reinforced by iron mesh | 0
| €/m3 | Parametric cost for: Mixing, laying and compacting C-25 (Rck 250) cement concrete including transport of materials and head carry to the site.
| m3 | Volume of Mixing, laying and compacting C-25 (Rck 250) cement concrete including transport of materials and head carry to the site.
| € | Cost of Mixing, laying and compacting C-25 (Rck 250) cement concrete including transport of materials and head carry to the site. | 0
| €/m2 | Parametric cost for: Supplying fabricating and fixing form work with plywood sheets of 12 mm thick inclusive of struts and removing the same.
| m2 | Surface of Supplying fabricating and fixing form work with plywood sheets of 12 mm thick inclusive of struts and removing the same.
| € | Cost of Supplying fabricating and fixing form work with plywood sheets of 12 mm thick inclusive of struts and removing the same. | 0
| €/kg | Parametric cost for: Cutting, bending, fabricating and placing tore steel reinforcements (Feb44K) including transport to the site
| kg | Weight of tore steel reinforcements (Feb44K) including transport to the site
| € | Cost of Cutting, bending, fabricating and placing tore steel reinforcements (Feb44K) including transport to the site | 0
Waterproofing | €/m2 | Parametric cost for: Supply and placing of HDPE membrane for pond waterproofing, min tickness 1.5 mm, including welding and testing
| m2 | Surface of Supply and placing of HDPE membrane for pond waterproofing, min tickness 1.5 mm, including welding and testing
| € | Cost of Supply and placing of HDPE membrane for pond waterproofing, min tickness 1.5 mm, including welding and testing | 0
| €/m2 | Parametric cost for: Supply and placing layers of pervious felt (nonwooven geotextile) (300 gr/m2)
| m2 | Surface of Supply and placing layers of pervious felt (nonwooven geotextile) (300 gr/m2)
| € | Cost of Supply and placing layers of pervious felt (nonwooven geotextile) (300 gr/m2) | 0
Manhole | €/unit | Parametric cost for: Procurement of precast concrete manhole 1x1x1 m, including concrete slab and covering
| n° unit | number of manholes
| € | Cost of manholes | 0
Pipelines and hydraulic works | €/m | Parametric cost for: supply and placing PVC pipe DN160 for gravity installation
| m | Length of PVC pipe DN160 for gravity installation
| € | Cost of PVC pipe DN160 for gravity installation | 0
| €/m | Parametric cost for: supply and placing HDPE pipe DN90 for pressure operating
| m | Length of HDPE pipe DN90 for pressure operating
| € | Cost of HDPE pipe DN90 for pressure operating | 0
Plants | €/unit | Parametric cost for: Procurement and placing of Phragmites Australis in pots 9 cm
| n° unit | number of Phragmites Australis
| € | Cost of Phragmites Australis | 0
Manwork | €/h | Parametric cost for: Man work - qualified worker
| h | number of hours per Man work - qualified worker
| € | Cost of Man work - qualified worker | 0
| €/h | Parametric cost for: Man work - unqualified worker
| h | number of hours per Man work - unqualified worker
| € | Cost of Man work - unqualified worker | 0
Total CAPEX | € |  | 0
Specific TOTAL CAPEX | €/m2 |  | 0 | Square meter of net CW surface
Specific TOTAL CAPEX | €/m2 |  | 155 | From Greek Case Study
COSTS (OPEX)
Paramenter to analyse | Unit | Specification | Amount used | Unit Value | Total Cost | Notes
Reagents | €/y | Considering reagents both for operation and maintenance (cleaning) | None | None | 0 | l/y*€/l
Energy costs | €/y | Considering cost of electricity [average between day and night, during week and week-end] |  |  | 0 | kWh/y * €/kWh(=0,17 average in Europe for non-household elecrticity)
Human Requirement | €/y | Considering personnel both for operation and maintenance |  |  | 0 | Hour of work required/y (MAX) * €/h
Maintenance | €/y | Manholes cleaning + maintenance of electromechanical components+maintenance of concrete structures, sewer, embankments | - | - |  | Costs exclude the sampling.
Reed harvesting | €/y | Harvesting, transport, load, unload and disposal in landfill
Green maintenance | €/y | Harvesting, transport, load, unload and disposal in landfill
TOTAL ANNUAL OPEX | €/y |  | - | - | 0
Specific TOTAL ANNUAL OPEX | €/m2y |  |  |  | 0
TOTAL ANNUAL OPEX | €/m2y |  |  |  | 3.4 | From Greek Case Study
SYSTEM

## POST-TREATMENTs
GUIDANCE METHODOLOGY
1 a) DESIGN PHASE - TECHNICAL DATA
HYDRO 1 Facility n° | TECHNOLOGIES INVOLVED |  |  | Legend
1) | Upflow Anaerobic Sludge Blanket |  |  |  | Design Data which should be provided by the site manager
2) | Biogas Upgrading System |  |  |  | Assumed Data for Design phase
3) | Constructed Wetland
4) | Membrane/Sand Filtration + UV Disinfection
5) | Composting system
Design Data MEMBRANE UF
Parameters | Units | Typical | Used for HYDRO 1 in Greek Case Study | Insert Data according to Replication Site Case Study | Notes
Population equivalent to be served | PE |  | 500
Influent Wastewater Charateristics:
Flowrate | m3/d | - | 100
COD concentration | mg/l | - | 17.3
BOD5 concentration | mg/l | - | 9.9
TSS concentration | mg/l | - | 22.5
Organic Load | kg COD/d | - | 1.73
pH | - | - | 7.3
Conductivity | μS/cm | -
TKN Concentration | mg/l | - | 21
Ammonia Concentration | mg/l | - | 23
Operative Parameters
Specific Flowrate | l/m2 d | - | 4320
Membrane area | m2 | - | 40
Flowrate per module | m3/d | - | 172.8
n° of modules | n° | - | 0.5787
Filtered water tank | m3 | - | 1
Alternatively to the UF, Sand Filtration could be chosen according to local reclaimed water quality standards
Design Data SAND FILTRATION
Parameters | Units | Typical | Used for HYDRO 1 in Greek Case Study | Insert Data according to Replication Site Case Study | Notes
Population equivalent to be served | PE |  | 500
Influent Wastewater Charateristics:
Flowrate | m3/d | - | 100
COD concentration | mg/l | - | 17.3
BOD5 concentration | mg/l | - | 9.9
TSS concentration | mg/l | - | 22.5
Organic Load | kg COD/d | - | 1.73
pH | - | - | 7.3
Conductivity | μS/cm | -
TKN Concentration | mg/l | - | 21
Ammonia Concentration | mg/l | - | 23
Operative Parameters
Additional Disinfection Unit could be implemented to reclaimed water reuse in agriculture
Design Data UV
Parameters | Units | Typical | Used for HYDRO 1 in Greek Case Study | Insert Data according to Replication Site Case Study | Notes
Influent Wastewater Charateristics:
Flowrate | m3/d | - | 100
TSS concentration | mg/l | < 1 - 5 | 2
Water trasmittance (UVT) | % | > or = 55 | 75
Minimum Dose to ensure for discharge limit | mWxs/cm2 | - | 50
Design
The design of the lamps was done by analysing the Characteristic Curve of the lamp, provided by Supplier. The Curve has to be chosen according to the value of the UVT of the water to be treated. With this curve and with the value od the minimum dose to have a certain quality of the effluent, the treatable flowrate is detected. Thus with the information of the volume treated by ech lamp, the number of needed lamps is calculated.
MASS AND ENERGY BALANCE
| INPUTs |  | OUTPUTs |  |  | *Waste indicates any generic residual/or untreated flow which could be derived by the process
CW Effluent [m3/d] = | 0 |  | Water for irrigation [m3/d] = |  |  | If any, please indicate the type and the amount
Maximum Energy Needed [kWh/d] = | 0 |  | Energy Produced [kW/d] = | 0
|  |  | Backwash discharge [m3/d] = | 8 | to be recirculate to UASB
Technical minimum requirement to Technology replicability:
FOOTPRINT
Paramenter to analyse | Unit | Specification | TOTAL | Notes
Equipment area requirement | m2 | pumps
tanks
Cartridge microfilter for UF
Ultrafiltration membrane module/ Sand filtration module
UV Lamp
area for piping
PLC
Compact skid for the assembly of main units
Total area requirement | m2 | Considering all of the equipments (tanks. pumps. piping. etc...) | 0
Specific area equirement | m2/(m3treated/d) | m2 per m3/day of wastewater treated | 0.116 | From Greek Case Study
INPUTS (Requirements)
Paramenter to analyse | Unit | Specification | TOTAL | Notes
Influent Flowrate | m3/d | From Constructed Wetlands
Maximum Energy Consumption | kWh/d | Energy for: | kW absorbed | h/d | kWh/d | Notes
|  | pumps |  |  | 0 | kW*h/d
|  | UF system/sand filtration |  |  | 0
|  | UV System |  |  | 0
|  | PLC, sensors |  |  | 0
|  | TOTAL requirements |  |  | 0
Specific Energy consumption | kWh/m3 treated | Specific kWh consumed/day per m3/day of wastewater treated | - | - | 0.71708 | From Greek Case Study
Reagents Consumption | l/y | NaOH - Reagent for UF membrane maintenance (CEB)
| l/y | HCl - Reagent for UF membrane maintenance (CEB)
| l/y | NaOCl - Reagent for UF membrane maintenance (CIP)
OUTPUTS EXPECTED
Paramenter to analyse | Unit | Specification | TOTAL | Notes
Effluent Flowrate from Post-treatment | m3/d |  | 100
COSTS (CAPEX)
Paramenter to analyse | Unit | Specification | TOTAL | Notes
| € | tanks
| € | Cartridge microfilter for UF
| € | pumps
| € | Ultrafiltration membrane module/ Sand filtration module
| € | UV Lamp
| € | Piping, cables, valves
| € | Sensors
Construction/Installation of units | € | Preparation of site
| € | Installation
Total CAPEX | € |  | 0
TOTAL CAPEX | €/PE |  | 70 | From Greek Case Study
COSTS (OPEX)
Paramenter to analyse | Unit | Specification | Amount used | Unit Value | Total Cost | Notes
Reagents | €/y | NaOH - Reagent for UF membrane maintenance (CEB) |  |  | 0 | l/y*€/l
| €/y | HCl - Reagent for UF membrane maintenance (CEB) |  |  | 0 | l/y*€/l
| €/y | NaOCl - Reagent for UF membrane maintenance (CIP) |  |  | 0 | l/y*€/l
Energy costs | €/y | Considering cost of electricity [average between day and night, during week and week-end] |  |  | 0 | kWh/y * €/kWh(=0,17 average in Europe for non-household elecrticity)
Human Requirement | €/y | Considering personnel both for operation and maintenance |  |  | 0 | Hour of work required/y * €/h
Maintenance | €/y | Considering substitution of pieces etc… |  |  | 0 | Quantity of unit to change/y * €/unit
TOTAL ANNUAL OPEX | €/y |  |  |  | 0
TOTAL ANNUAL OPEX | €/y/PE |  |  |  | 0
SYSTEM

## COMPOSTING SYSTEM
GUIDANCE METHODOLOGY
1 a) DESIGN PHASE - TECHNICAL DATA
HYDRO 1 Facility n° | TECHNOLOGIES INVOLVED
1) | Upflow Anaerobic Sludge Blanket |  |  | PLEASE PRIVE INFO ON THIS SYSTEM
2) | Biogas Upgrading System
3) | Constructed Wetland |  |  | Legend
4) | Membrane/Sand Filtration + UV Disinfection |  |  |  | Design Data which should be provided by the site manager
5) | Composting system |  |  |  | Assumed Data for Design phase
Design Data
Parameters | Units | Typical | Used for HYDRO 1 in Greek Case Study | Insert Data according to Replication Site Case Study | Notes
Population equivalent to be served | PE |  | 500
Influent sludge Charateristics:
Flowrate | m3/d | -
COD concentration | mg/l | -
BOD5 concentration | mg/l | -
TS concentration | % | -
Sludge density | kg/m3 | -
Organic Load | kg COD/d | -
Sludge load | kg/d | -
pH | - | -
Conductivity | μS/cm | -
TKN Concentration | mg/l | -
Ammonia Concentration | mg/l | -
Operative Parameters
MASS AND ENERGY BALANCE
| INPUTs |  | OUTPUTs |  |  | *Waste indicates any generic residual/or untreated flow which could be derived by the process
Excess sludge from UASB [kgTSS/d] = | 2.5085
Excess sludge from UASB [m3/d] = | 0.12543 |  | Compost [kgTSS/d] = |  |  | If any, please indicate the type and the amount
Compost [m3/d] =
Othe material for composting [kgTSS/d] =
Othe material for composting [m3/d] =
|  |  | Energy Produced [kW/d] = | 0
Maximum Energy Needed [kWh/d] = | 0
|  |  | Waste* [.../d] = | 8
Technical minimum requirement to Technology replicability:
FOOTPRINT
Paramenter to analyse | Unit | Specification | TOTAL | Notes
Equipment area requirement | m2 | composting system
tanks
….....
Specific area equirement | m2/(m3treated/d) | m2 per m3/day of wastewater treated |  | From Greek Case Study
Total area requirement | m2 | Considering all of the equipments (tanks. pumps. piping. etc...) | 0
INPUTS (Requirements)
Paramenter to analyse | Unit | Specification | TOTAL | Notes
Influent Flowrate | m3/d
Energy Consumption | kWh/d | Energy for: | kW absorbed | h/d | kWh/d | Notes
|  | pumps |  |  | 0
|  | tanks |  |  | 0
|  | sensors |  |  | 0
….......
|  | TOTAL requirements |  |  | 0
Specific Energy consumption | kWh/m3 treated | Specific kWh consumed/day per m3/day of wastewater treated | - | - | #DIV/0! | From Greek Case Study
Reagents Consumption | l/d | Considering reagents both for operation and maintenance (cleaning) | None
OUTPUTS EXPECTED
Paramenter to analyse | Unit | Specification | TOTAL | Notes
Effluent Flowrate from Post-treatment | m3/d |  | 0
COSTS (CAPEX)
Paramenter to analyse | Unit | Specification | TOTAL | Notes
Cost of units | € | tanks
| € | pumps
| € | ….....
| € | …....
Construction/Installation of units | € | Preparation of site
| € | Installation
Total CAPEX | € |  | 0
TOTAL CAPEX | €/PE |  | #DIV/0! | From Greek Case Study
COSTS (OPEX)
Paramenter to analyse | Unit | Specification | Amount used | Unit Value | Total Cost | Notes
Reagents | €/y | Considering reagents both for operation and maintenance (cleaning) |  |  | 0 | l/y*€/l
Energy costs | €/y | Considering cost of electricity [average between day and night, during week and week-end] |  | 0.17 | 0 | kWh/y * €/kWh(=0,17 average in Europe for non-household elecrticity)
Human Requirement | €/y | Considering personnel both for operation and maintenance |  |  | 0 | Hour of work required/y * €/h
Maintenance | €/y | Considering substitution of pieces etc… |  |  | 0 | Quantity of unit to change/y * €/unit
TOTAL ANNUAL OPEX | €/y |  |  |  | 0
TOTAL ANNUAL OPEX | €/y/PE |  |  |  |  | From Greek Case Study
SYSTEM

## AGROFORESTRY &IRRIGATION SYSTEM
GUIDANCE METHODOLOGY
1 a) DESIGN PHASE - TECHNICAL DATA
HYDRO 1 Facility n° | TECHNOLOGIES INVOLVED |  |  | Legend
1) | Agroforestry and irrigation system |  |  |  | Design Data which should be provided by the site manager
Assumed Data for Design phase
Design Data
Parameters | Units | description | Used for HYDRO 1 in Greek Case Study | Insert Data according to Replication Site Case Study | Notes
Area to be irrigated | ha
Type of crops to be irrigated | - | forestry trees for fruit and timber production; orchards/bushes; and herbs and annual crops.
Irrigation system | - | type of irrigation system
Water need of the crops | m3/ha or m3/m2 | irrigational needs
Nutrient need of the crops | kgN/ha or kg/m2 | nitrogen need for crops and plants
Technical minimum requirement to Technology replicability:
FOOTPRINT
Paramenter to analyse | Unit | Specification | TOTAL | Notes
Equipment area requirement | m2 | area to be irrigated
tanks
…..........
Specific area equirement | m2/(m3treated/d) | m2 per m3/day of wastewater treated |  | From Greek Case Study
Total area requirement | m2 | Considering all of the equipments (tanks. pumps. piping. etc...) | 0
INPUTS (Requirements)
Influent Flowrate | m3/d
Energy Consumption | kWh/d | Energy for: | kW absorbed | h/d | kWh/d | Notes
|  | pumps |  |  | 0
|  | ….... |  |  | 0
TOTAL requirements
Specific Energy consumption | kWh/m3 treated | Specific kWh consumed/day per m3/day of wastewater treated | - | - |  | From Greek Case Study
Reagents Consumption | l/d | Considering reagents both for operation and maintenance (cleaning) | None | None | None
OUTPUTS EXPECTED
Effluent Flowrate from Post-treatment | m3/d |  |  |  | 0
COSTS (CAPEX)
Cost of units | € | tanks |  |  | 0
| € | pumps |  |  | 0
| € | …......... |  |  | 0
Construction/Installation of units | € | Preparation of site |  |  | 0
| € | Land purchase |  |  | 0
| € | Installation |  |  | 0
Total CAPEX | €
TOTAL CAPEX | €/PE |  | - | - |  | From Greek Case Study
COSTS (OPEX)
Reagents | €/y | Considering reagents both for operation and maintenance (cleaning) |  |  | 0 | l/y*€/l
Energy costs | €/y | Considering cost of electricity [average between day and night, during week and week-end] |  | 0.17 | 0 | kWh/y * €/kWh(=0,17 average in Europe for non-household elecrticity)
Human Requirement | €/y | Considering personnel both for operation and maintenance |  |  | 0 | Hour of work required/y * €/h
Maintenance | €/y | Considering substitution of pieces etc… |  |  | 0 | Quantity of unit to change/y * €/unit
Insurance | €/y |  |  |  | 0
ANNUAL TOTAL OPEX | €/y |  |  |  | 0
ANNUAL TOTAL OPEX | €/y/PE |  |  |  |  | From Greek Case Study

## Mass and Energy Balance
GUIDANCE METHODOLOGY
ENERGY and MASS BALANCE
[6 empty] | BIOGAS | [5 empty] | Thermal Energy Produced
[6 empty] | Q | m3/d
[6 empty] | %CH4 | % |  |  |  |  | kWh/d
[6 empty] | %CO2 | %
|  |  |  | GASOMETER |  | %H2S | %
|  |  |  | Energy consumption | kWh/d |  |  | CHP
Electricity Produced
[8 empty] | Energy consumption | kWh/d
kWh/d
BIOGAS
|  | Q | m3/d
|  | %CH4 | %
|  | %CO2 | %
|  | %H2S | %
[6 empty] | MUNICIPAL WASTEWATER |  |  |  | MUNICIPAL WASTEWATER |  |  |  |  | MUNICIPAL WASTEWATER
[6 empty] | Q | m3/d |  |  | Q | m3/d |  |  |  | Q | m3/d
[6 empty] | COD | mg/L |  |  | COD | mg/L |  |  |  | COD | mg/L
[6 empty] | Ntot | mg/L |  |  | Ntot | mg/L |  |  |  | Ntot | mg/L
| MUNICIPAL WASTEWATER |  |  |  |  | Ptot | mg/L |  |  | Ptot | mg/L |  |  |  | Ptot | mg/L |  |  | RECLAIMED WATER
| Q | m3/d |  | UASB |  | TSS | mg/L | WETLAND |  | TSS | mg/L |  | ULTRA FILTRATION/ SAND .. |  | TSS | mg/L | DISINFECTION |  | Q | m3/d
| COD | mg/L |  |  |  | E.coli | 100 UFC/mL |  |  | E.coli | 100 UFC/mL |  |  |  | E.coli | 100 UFC/mL |  |  | COD | mg/L
| Ntot | mg/L |  | Energy consumption | kWh/d |  |  | Energy consumption | kWh/d |  |  |  | Energy consumption | kWh/d |  |  | Energy consumption | kWh/d | Ntot | mg/L
| Ptot | mg/L | [16 empty] | Ptot | mg/L
| TSS | mg/L | [16 empty] | TSS | mg/L
| E.coli | 100 UFC/mL | [16 empty] | E.coli | 100 UFC/mL
AGROFOSTERY SYSTEM
|  | SLUDGE | [18 empty] | Energy consumption | kWh/d | CROP AND PLANTS
|  | Q | m3/d | [19 empty] | Type | -
|  | TSS | kgTSS/d | [19 empty] | Production | kg/y
|  | %TS | %
|  |  |  | COMPOSTING SYSTEM | [14 empty] | COMPOST
[19 empty] | Q | m3/d
|  |  |  | Energy consumption | kWh/d

## Business model
TOTAL HYDRO CAPEX summary | [7 empty] | Comments
Total CAPEX | [5 empty] | #REF! | €
TOTAL HYDRO OPEX summary
System Operation | [5 empty] | #REF! | €/year
Insurance | External services |  |  |  |  | 0 | €/year
Certification/permit fees | External services |  |  |  |  | 0 | €/year
Yearly OPEX | [5 empty] | #REF! | €/year
Revenue & costs saving streams
|  | Unit | Quantity | Item value* | Unit | Revenue | revenue unit | * from Local market analysis
Treated wastewater for irrigation |  | m3/year |  |  | €/m3 | 0 | €/year
Biogas |  | MWh/year |  |  | €/MWh | 0 | €/year
Fertilizers |  | kg/year |  |  | €/kg | 0 | €/year
Waste water treatment tax |  | m3/year |  |  | €/m3 | 0 | €/year
Annual food production from crop cultivation |  | kg/year |  |  | €/kg | 0 | €/year
Yearly revenues | [5 empty] | 0 | €/year
Payback period |  | year | #REF! | CAPEX/(yearly revenues - OPEX)