## Slide 1
HYDRO 1
a sewage treatment system applied in decentralised areas with high seasonal loads to recover energy and recycle water and nutrients
System Description
HYDRO1 consists of a sewage treatment system applied in decentralised areas with high seasonal loads. HYDRO1 combines anaerobic processes (Upflow Anaerobic Sludge Blanket (UASB) reactor) with constructed wetlands and disinfection to treat domestic wastewater as a completely circular solution, where water, nutrients and the produced sludge are going to be reused. Furthermore, the anaerobic process recovers energy in the form of biogas.
HYDROUSA establishes the optimal operating conditions under which organic load removal and biogas production are maximized. The excess sludge from the UASB gets mixed with biomass and co-composted in an innovative in-vessel composting system, coupled with a novel plant biofilter to treat the odours. According to legal constraints the UASB effluent will be either treated in a series of saturated and unsaturated constructed wetlands (CWs), filtered and disinfected for reuse in agriculture, or will be directly used for fertigation after disinfection. The produced biogas may be used for energy production in CHP generators or can be upgraded to methane to be valorised as a fuel. A simplified layout of HYDRO 1 is shown in Figure 1.
Possible by-pass
Municipal waste
water
UASB
Constructed Wetltand
Gasometer
Scrubber + Stripper for biogas upgrade
Gas Compression
Ultra Filtration Membrane
UV Disinfection
Composting System
Biomethane for reuse as biofuel
Water for irrigation
Compost

## Slide 2
Technical Specifications
UASB
Pretreatment requirements: grease and grit removal
Municipal wastewater temperature range = 15–35 °C
Hydraulic Residence Time = 7 – 10 h
Organic loading = 2 - 10 kgCOD/m3/day
Area required = 0.25 m2 per m3/day of wastewater treated
Upflow velocity = 0.5–1 m h-1
Organic pollution removal as COD = 70 – 80%
Solids removal as TSS = 70 – 80%
Biogas production = 0.24 m3 biogas per m3 of wastewater treated
Sludge production = 25 g DS per m3 of wastewater
Constructed Wetlands
Area required = 8.5 m2 per m3/day of wastewater treated
Organic pollution removal as COD = 90%
Solids removal as TSS = 75%
Nitrogen removal = 10-20% (one stage wetland);
50-70% (two-stage wetland)
E. coli removal = 90 – 99%
Sludge production = none
Post-treatment
Ultrafiltration membrane
TSS removal = 96 – 99%
Total and Fecal Coliforms reduction = 3 – 6 log
Rate of flux = 60 – 180 l m-2h-1
Energy consumption = 0.2 – 0.3 kWh m-3 of wastewater treated
UV Lamp
Estimated lamp life = 8000 – 12,000 hours
Max Energy consumption = 0.03 kWh m-3 of wastewater
Benefits
No wastewater discharge into the sea at dry weather
High quality wastewater effluent that meets Directive 91/271 effluent criteria
Cheaper Production of reclaimed water for restricted and unrestricted irrigation
Recycling nutrients in agriculture
Low energy consumption < 0.3 kWh/m³ of wastewater treated
Energy recovery from wastewater = 0.6 kWe/ m³ of wastewater treated
Low O&M costs < 0.5 €/m³ of wastewater treated
Pay back period < 9 years